Blue-White Series-M

CHEM-FEED model MD-3 Diaphragm Metering Pump

- METERING PUMP – Shall be a Dual-Diaphragm type pump with a variable speed DC motor, no loss motion positive pull-back cam drive mechanism, double ball inlet and outlet cartridge type check valves, and integral diaphragm leak detection system. Chem-Feed MD-3 model shall be capable of output volumes to 52.6 gallons per hour and back pressures to 145 PSI (10 bar).

  - Capable of running dry without damage.

  - Output adjustment range shall be from 0.05 to 100% in 0.1% increments. 2,000:1.

  - Dual diaphragm design shall provide near continuous chemical output.

  - Pump shall be rated for continuous duty.

  - Quiet, low pulsation/low velocity output.

  - Suction lift shall be 23 feet of water (at sea level)

  - Maximum fluid viscosity shall be 1000 centipoises.

  - Pump shall have a 5-year manufacturer’s warranty.

- PUMPHEAD

  - The pumphead shall be manufactured from natural PVDF material.

  - The diaphragm shall be manufactured from a single layer of DiaFlex PVDF material or Flex-A-Prene material. Laminated diaphragms shall not be used.

  - The inlet and outlet pump head valve housings shall be manufactured from natural PVDF material.

  - The dual pump head inlet valve housings and outlet valve housings shall be connected by a PVDF manifold pipe.

  - The pump inlet (suction) adapter and the outlet (discharge) adapters may be installed in the field on either the left or right side of the pump.

  - The inlet and outlet adapters shall be available for ½” male NPT or ½” ID hose barb connections in elbow or straight configurations.

  - There shall be four check valve cartridge assemblies per pump head, two located in the inlet valve assembly and two located in the outlet valve assembly. Each cartridge check valve assembly shall contain a ceramic ball, static seal o-ring and ball seat o-ring. O-ring ball seats shall be manufactured from T/FEP (optional EP) elastomer material. Static adapter fitting seals shall be manufactured from FKM (optional EP) elastomer material. An optional Hastelloy spring-loaded single ceramic ball check valve shall be available. (Engineer to specify)

  - The pump head front shall be covered with a 316 Stainless Steel metal pressure support plate.

  - The pump head shall be positively secured to the pump housing with 8 each 10-32 stainless steel socket head screws and washers.

- DRIVE SYSTEM – Shall be factory installed and totally enclosed in a NEMA 4X, (IP66) wash-down enclosure. Capable of operating on any input power from 110VAC to 240VAC, 50/60 Hz single phase supply without user configuration or selection switches.

  - Motor

    - Brushless DC gear motor rated for continuous duty.

    - Motor shall include overload protection.

    - The maximum gear motor RPM shall be 190 RPM.

  - Drive mechanism

    - The drive cam shall apply force to a drive linkage which in turn moves two diaphragms through the suction and discharge strokes.

    - The drive cam shall provide the force for both the suction and discharge strokes, resulting in no loss of motion during the stroke.

    - The diaphragm stroke length shall be 0.190 inches at all times. Stroke length adjustment shall not be provided.

  - Enclosure

    - Bottom housing shall be pressure cast aluminum with acidic liquid iron phosphate three-stage clean and coat pretreatment and exterior grade corrosion resistant polyester polyurethane powder coat.

    - Top housing shall be structural foam molded Noryl engineered thermoplastic.

    - Rated NEMA 4X (IP66).

    - Provided with 316SS floor/shelf level mounting brackets and hardware.

    - M12 receptacles shall be located at the rear of the pump for input and output signals.

    - RJ45 receptacle shall be located at the rear of the pump for use with EtherNet/IP and Modbus TCP/IP

    - One M12 receptacle shall be located at the rear of the pump for use with Profibus

    - Provide an LED light for viewing the internal drive mechanism to confirm drive operation.

  - Control Circuitry. All control circuitries shall be integral to the pump.

    - All control circuitry shall be integral to the pump and capable of adjusting the pump motor speed from 0.05% to 100.0% in 0.001% increments less than 1% motor speed, in 0.01% increments between 1% and 10% motor speed, and in 0.1% increments greater than 10% motor speed (2,000:1 turndown ratio).

    - The pump output shall be capable of being manually controlled via front panel touchscreen. The pump motor speed shall be adjustable from 0.05% to 100.0% in 0.01% increments less than 10% motor speed and in 0.1% increments greater than 10% motor speed.

    - The pump output shall be capable of being remotely controlled via 4-20mA analog input. The input resolution shall be 0.01 of input value and capable of adjusting the pump motor speed from 0% to 100.0% motor speed in 0.1% increments. Four values shall be user configurable to define the low and high points on the output slope: a low input value, the required pump percentage of motor speed at the low input value, a high input value, the required pump percentage of motor speed at the high input value.

    - The pump output shall be capable of being remotely controlled via TTL/CMOS digital high-speed pulse type input and an AC sine wave type pulse input in the range of 0 to 1,000 Hz. The frequency resolution shall be 1 Hz and capable of adjusting the pump motor speed from 0% to 100.0% motor speed in 0.1% increments. Four values shall be user configurable to define the low and high points on the output slope: a low input value, the required pump percentage of motor speed at the low input value, a high input value, the required pump percentage of motor speed at the high input value.

    - The pump output shall be capable of being remotely controlled via pulse triggered batching. The pump shall accept a TTL/CMOS digital pulse type input and a contact closure type pulse input in the range of 1 to 5,629,499,534,21,312 pulses per batch. The batch time shall be adjustable from 1 to 5,629,499,534,21,312 seconds. The pump motor speed during the batch shall be adjustable from 0% to 100.0% motor speed in 0.1% increments.

    - Pump shall be capable of remote priming via non-powered contact closure loop

    - The pump output shall be capable of being controlled via EtherNet/IP, Modbus TCP/IP, or Profibus. Device configuration shall be as follows:

Control and Status Mapping for Profibus and EtherNet/IP:

Control and Status Mapping for Modbus TCP/IP

    - Provide a front panel touchscreen control for stop/start, configuration menu access and navigation, operating mode selection, display options selection, tube info data, and reverse direction.

    - Provide a multi-color LCD touchscreen display for menu driven configuration settings, pump output value, service alerts, diaphragm failure detection (DFD) system and flow verification system (FVS) alarms status, remote input signal values, run timer value. Display color shall be green when indicating run operation, blue when in idle, yellow when in stand-by, and red to indicate an alarm condition exists.

    - Provide for remote stop/start pump via non-powered contact closure loop.

    - Provide a user selectable 4-20mA and 0-1,000Hz output signal which are scalable and proportional to pump output volume.

    - Provide four contact closure alarm outputs. Three rated at 1A-115VAC, 0.8A-30VDC and one rated at 6A-250VAC, 5A-30VDC. Each alarm output shall be assignable to monitor any of the following pump functions: TFD system, FVS system, motor run/stop, motor failed to respond to commands, motor is running in reverse, general alarm (TFD, FVS, and/or motor over current), input signal failure, output signal failure, remote/local control status, stroke counter (life) set-point, or monitor which of the nine different pump operating modes is currently active.

    - Provide a six-digit password protected configuration menu.

    - Provide a flow verification system with programmable alarm delay time from 1-1000 seconds. FVS system shall monitor the FVS flow sensor while pump is running only. System shall not monitor pump while not running.

- FLOW VERIFICATION SENSOR – Shall output high-speed digital pulse signal or 4-20 mA, while pump is running only, to verify chemical injection.

  - Flow verification sensor shall be an ultrasonic transit time sensor.

  - Wetted components shall be PVDF (optional PVC), PEEK, and TFE/P (optional EP).

  - End fittings shall be PVDF with optional PVC slip fittings. All are included.

  - Sensor operating range shall be as follows: (Engineer to specify)

Code		Flow Range (GPH)	 Flow Range (LPH)	    Flow Range (mL/min)

A				0.158-79.2				0.597-299.4				10.0-5,000

B				1.580-158.5			5.970-600.0				100-10,000

  - Shall provide a scalable 4-20 mA sourcing output.

  - Shall provide a scalable 0-10,000 Hz open collector frequency output

  - Shall provide a programmable Form C Solid State Relay rated for a maximum load capacity of 24 VDC and 100 mA.

    - Programmable for high/low flow rate alarm.

    - Programmable to energize on specified flow total.

  - Power Requirements: 5-24 VDC; 5 Watts maximum.

- SAFETY

  - The pump shall be certified to NSF Standard 61 Drinking Water System Components, UL standard 778 as a motor operated pump and CSA standard C22.2 as process control equipment.

  - Diaphragm Failure Detection (DFD) system sensors shall be wholly located in the pumphead. DFD system will stop the pump within three seconds of leak detection. To prevent false alarms due to rain, wash-down, condensation, etc., tube failure detection system shall not trigger with water contact.

- Manufacturer

  - The pump shall be Blue-White Chem-Feed M diaphragm pumps, manufactured wholly in the U.S.A. by Blue-White Industries, Huntington Beach, CA.